## SINEXHELL 1ph NOTES
The current version of code found in the OpenEMS GitHub is still the code we started with, for the old inverter protocol. It is identical to the code before I started changing it for the new v120 protocol
To be clear, my branch (jimstercoder) is the only branch with code for the new V120 protocol.
I 'privitized' my version of OEMS prior to making changes for single phase operation

## Work List
James				Niall
Priority Rating	Job	Notes		Priority Rating	Job	Notes
0	What does FENECON use to interact with the scheduler?	Scheduler only seems to have the unfriendly json editing inteface.		Chase a contact at Openstar
0	Verify that the TSUN used the Pylon protocol.			Find customers
0	Will existing BC operate one Leaf Battery with internal contactors?	What action would cause the contactors to open? (as there will be no shunt)		Write 40 Page IM for $5million Machine
0	For a multi-battery system is it practical/acceptable to control the pre-charge contactor with a common output to all batteries?			Write code to analyse data for $5 million Machine
0	How much work to move inverter CAN comms to run off of the Teensy?			Create business model & business case for $5million machine
1	Make the graph much prettier - grafana or similar. This is our marketing and people care a lot about looks. Better marketing = better chance of $$			Create Graphics for IM
3	Look into GoodWe inverter integration in OEMS			Read WEL machine specs. Comment/propose solutions
4	Look into Deye inverter integration in OEMS... is it working (Angel is working on it)	email Angel & ask how its going. Don't spend more time on it than this. GoodWe may be a good option too hence not spending time on Dye.		Provide james with data capture specs
5	Research Pi5 for edge & backend	-do we even need Backend for a small system? Can we run UI without backend, as is done in the simulator? (and still have the functionality we need)
7	Create separate Sinexcl component in OEMS for the new inverter (the code I wrote/modified)
8	Create a web interface for the BatteryController, to replace the console interface	As I found a way to start BC with a console display this may not be necessary

Completed				Completed
	Look into recording Turners Auctions similar to Manheim
	Need to test the JAR files I generated on the command line using gradle	This seems to be a bust as I found that gradle only works if the code has been compiled with Eclipse first. That is, a raw project downloaded from Github will not compile with gradle. I wrote a proceedure (see Force Recompiile tab) on how to force a complete compile with Eclipse. This is necesesary as Eclipse also fails to compile after some changes have been made to the code. It's a shyte situation.		Meet with Vector to understand connections for $5million machine
	Complete the python code to talk REST api to OEMS for controlling the inverter
	Get WITS API code working
	Get BatteryController to auto start on the Pi.
	Get OEMS Edge to auto start on Pi (this involves auto installing Java 17)
	Get the UI backend to autostart on the Server
	Update graphs as per email 1st Aug 24 (or see note attached to this cell)
		Use the Apache Felix OSGi Management Console tab in the Apache Felix Web Console Configuration webpage ie http://192.168.2.14:8079/system/console/configMgr
1	Make a page for yesterday's info with only the existing two top charts on it. Maintain the same web address for this. https://jimster.ca/BatteryOne/BatteryOneAll.php?time=yd / This is to simplify what non-technical people see and because I have shared the adress a alot I don't want it changing.	James: (DOES) What you mean is change the yesterdays chart to have only the to two charts. / Niall: Yes

## WITS Auth
Client ID	Client Secret
tT8H6PNzdopboFB7DMKlb8VrepoZzh7i	pQvEqET13OoFpUNLH6dwqlS8t24n08QG

## BatteryController Safety
Battery Controller Safety Features

Battery Status data is recieved from the Leaf BMS by BatteryController via CAN bus communications
The BMS data is used to make control decisions as well as passed on to the inverter

The CONTACTORS connecting the array of batteries to the inverter will be opened on the following conditions
1.	Loss of CAN communications with the inverter
	-if no CAN mesage is received for 60 seconds VERIFY THIS VALUE

The SHUNT for a particular battery is tripped (open circuited) on the following conditions

1.	Loss of CAN communications with battery
	-if no CAN message is received for 60 seconds					PACK_SILENT_TIMEOUT_PERIODS

2.	Over Temperature
	-if the battery temperature measured by the BMS exceeds 50 degC					CRITICALLY_HIGH_TEMPERATURE

3.	Under Temperature
	-if the battery temperature measured by the BMS goes below 2 degC					CRITICALLY_LOW_TEMPERATURE

4.	Missing Sensors					MAX_TEMP_SENSORS_MISSING
	-if more than 1 of the temperature sensors fails to report a value

5.	Cell Over Voltage
	-if the BMS reports a cell voltage of more than 4.15v					CRITICALLY_HIGH_VOLTAGE

6.	Cell Under Voltage
	-if the BMS reports a cell voltage of less than 3.0v					CRITICALLY_LOW_VOLTAGE

7.	Excessive Cell Voltage Spread
	-if the battery's MaxV - MinV exceeds 0.5v					CRITICALLY_HIGH_VOLTAGE_SPREAD

	Note on Charge/Discharge Current Limit
	-the Battery Controller relays the requested charge current limit from the BMS to the Inverter
	-there is a 30A fuse in place to restrict the battery current to that value

## MeterSDM630
CT Setting
The CT setting has to be changed in the meter
-The CT says 150A/5A
-CT2 has to be set to 5 (which it is by default)
-CT Rate has to be set to 30 = 150/5 (default is 1)

Baud Rate
-set the correct baud rate!
-this must match what is set in Bridge Modbus/RTU Serial in OpenEMS back end
-I have decided to use 38.4k as this is the default rate for the Zigbee radios

## Ubuntu Install
Install and configure Ubuntu 22.04 LTS for Battery Project

Get VM
Update software using 'Software Update Application

sudo apt update
sudo apt install -f

Change passward to oov "sudo passwrd" ignore warnings, enter now password

Install Github Desktop using .deb file "sudo dpkg -i <filename>.deb"
https://meshworld.in/install-github-desktop-on-ubuntu-20-04-or-ubuntu-based-distributions/

Install java "java -version" to check then install using "sudo apt install openjdk-17-jre-headless"

Install VSCode "sudo snap install code --classic"

Install Eclipse for Java, use the tar method "./eclipseinst"
https://linux.how2shout.com/2-methods-to-install-eclipse-ide-on-ubuntu-22-04-or-20-04-lts/

Setup Eclipse for OpenEMS
https://openems.github.io/openems.io/openems/latest/gettingstarted.html

sudo apt -y install cmake
sudo apt -y install build-essential
sudo apt -y install libsocketcan-dev
libgpiod-dev
can-utils
libmodbus-dev
sudo apt-get install libncurses5-dev libncursesw5-dev
sudo apt install valgrind libcurl4-openssl-dev

Install CH340 driver
https://0xsuk.github.io/posts/2022-07-19-how-to-install-ch340-on-ubuntu-22.04/

install pkgconf - this is needed to compile sdm120c
sudo apt install pkgconf

On 22.04 you have to give user access to dialout group to access ttyUSB0. you have to REBOOT after doing this.
sudo usermod -a -G dialout $USER
sudo reboot

INSTALLING node.js
Download from https://nodejs.org
Install Procedure
https://github.com/nodejs/help/wiki/Installation
/.profile in a hidden file in the /home directory. press Ctrl-H to reveil it and use texteditor to edit it.

## RPi Install
Configure a Raspbery Pi for TIML Battery Project Use

How at assign specific port name (serial number) to specific Teensy's
The stuff in green is not necessary but good to know, go to the orange 'Create a udev rule'.

Get info about the devices
udevadm info -a -n /dev/ttyACM0 >acm0
udevadm info -a -n /dev/ttyACM1 >acm1

Get more info
/dev......'/ below taken from the top of the acm0/1 files above
udevadm test '/devices/platform/soc/3f980000.usb/usb1/1-1/1-1.2/1-1.2:1.0/tty/ttyACM0' >t0
udevadm test '/devices/platform/soc/3f980000.usb/usb1/1-1/1-1.2/1-1.2:1.0/tty/ttyACM1' >t1

diff -u t0 t1
look for ID_SERIAL_SHORT this is unique to each teensy

Create a udev rule
sudo nano /etc/udev/rules.d/99-my-teensy.rules
put the below line in the file
(ok, you didn't actually have to do the stuff above I just noticed, but it's good know where this info came from)
SUBSYSTEM=="tty", ATTRS{idVendor}=="16c0", ATTRS{idProduct}=="0483", SYMLINK+="ttyTSY%E{ID_SERIAL_SHORT}"

reload the rules
sudo udevadm control --reload
reboot

Now you should get /dev/ttyTSY{serial number} for each teensy
ls -al /dev/ttyT*
lrwxrwxrwx 1 root root 7 Nov 7 13:46 /dev/ttyTSY11576900 -> ttyACM1
lrwxrwxrwx 1 root root 7 Nov 7 13:46 /dev/ttyTSY12508710 -> ttyACM0

Now, use the /dev/ttyTSYXXXXX name when starting testcan, making sure you know physcially which is which (duh).

How to install Java 17
https://foojay.io/today/java-17-on-the-raspberry-pi/
Following procedure based on the above information.

Install zip
sudo apt install zip

Install curl
sudo apt install -y curl

Install SDK
curl -s "https://get.sdkman.io" | bash
When I did this is did some stuff then failed. When I did it again it said to force an update.
sdk selfupdate force
After that, it installed successfully.

This command 'runs' sdk. It must be done everytime the Pi is booted and on the terminal you want to run java
source "$HOME/.sdkman/bin/sdkman-init.sh"
Check it is working
sdk version

See the javas available
sdk list java
At the time of this writting we were using 17.0.8.1-zulu
sdk install java 17.0.7-zulu
java -version

Startup Script to install CAN Drivers
create the .sh file to run your commands. BE SURE IT WILL NOT HANG
(get this file from an existing TIML pi, or /BatteryController/CANDriverInstall on github)
CANDriverInstall.sh

create the directory /home/pi/CANDriverScript
put CANDriverInstall.sh in that directory

edit /etc/rc.local
sudo nano /etc/rc.local
add the following lines above 'exit 0'
date >> /home/pi/CANDriverScript/BOOT-Msg.txt
sh /home/pi/CANDriverScript/CANDriverInstall.sh >> /home/pi/CANDriverScript/BOOT-Msg.txt 2>&1 &

make it executable
sudo chmod +x /etc/rc.local

reboot to test it
sudo reboot
check the log file to see if it ran
cat /home/pi/CANDriverScript/BOOT-Msg.txt

Make java 17 the default version when a shell starts up
-this isn't really necessary but is a nice to have

nano ~/.bashrc
add the following lines to the end of the file

# Initialize SDKMAN!
export SDKMAN_DIR="$HOME/.sdkman"
[ -s "$SDKMAN_DIR/bin/sdkman-init.sh" ] && source "$SDKMAN_DIR/bin/sdkman-init.sh"
# Set default Java version
sdk use java 17.0.7-zulu

save the file and reload the shell profile
source ~/.bashrc

you should see this when you start a shell

Auto start batterycontroller at boot time
the file start_battery_controller.sh should already be in the BatteryController directory
from the BatteryController directory issue the following commands
copy the service program to the system directory
sudo cp AutoStartupPi/start-battery-controller.service /etc/systemd/system
reload the service daemon so it sees the service
sudo systemctl daemon-reload
enable the service
sudo systemctl enable start-battery-controller.service
the service will now start when the pi is rebooted

now copy the scipt to use to stop the service
cp AutoStartupPi/stopbatterycontroller.sh /home/pi
it's best to stop the batterycontroller by pressing CTRL-C on the shell window (this caues a clean shutdown, which doesn't seem to happen consistantly when the service is stopped, as below)
but, if that's not possible, you can stop the batterycontroller by opening a new shell and use the command
sh stopbatterycontroller.sh

Examples of system service commands
sudo systemctl daemon-reload
sudo systemctl enable start-battery-controller.service
sudo systemctl start start-battery-controller.service
sudo systemctl stop start-battery-controller.service
sudo systemctl status start-battery-controller.service

Auto start OpenEMSEdge at boot time
from the BatteryController directory
copy the startup scipt to the openems directory
cp AutoStartupPi/start_openems_edge.sh /home/pi/openems
copy the service program to the system directory
sudo cp AutoStartupPi/start-openems-edge.service /etc/systemd/system

reload the service daemon so it sees the service
sudo systemctl daemon-reload
enable the service
sudo systemctl enable start-battery-controller.service
the service will now start when the pi is rebooted

as above... it's best to use CTRL-C to stop it but...
cp AutoStartupPi/stopopenemsedge.sh /home/pi
open a shell and use the command
sh stopopensedge.sh

How to upload to Teensy from RPi
Install apt to write .hex files to Teensy
assuming git is already installed
install usb library
sudo apt install libusb.dev

install loader app
git clone https://github.com/PaulStoffregen/teensy_loader_cli.git
cd teensy_loader_cli
make

get the firmware.hex file from the .pio /build/teensy40 hidden directory for the teensy project (using PlatformIO)
put it in the teensy_loader_cli directory

press the program button on the teensy, the led by the serial connector will go on dimly
below command will upload the file and reboot the teensy, it has no on screen feedback
./teensy_loader_cli --mcu=TEENSY40 -w /path/to/your/firmware.hex

to do the upload without pushing the program button use the below command
this won't work on a new or bricked teensy but should work to update firmware
on an already programmed teensy
./teensy_loader_cli --mcu=TEENSY40 -w -s -v firmware.hex

sample output for auto uploading

## Backend-Autostart
Enable 'ping' response
https://kb.iu.edu/d/aopy

NSSM is not longer used. Below are instructions to use a batch file to start jar files.
Use NSSM utility to install/delete service for java
https://nssm.cc/usage
This app was used to create a service for the openems-backend java app (jar file)
Need to document where the files are when I have access to the server again.
I think I set it up to log the output to a file that rolls over
There is a directory somewhere with NSSM.exe in it
Use windows service manager to change the settings on the service.

If using a WinDoze computer for backend read this!
You have to go into Device Manager, properties for the network card and disable sleeping of the network card

Disable Automatic Updates
To completely turn off Windows updates on Windows 10, you can use the Group Policy Editor to disable automatic updates. Here are the steps:
Open the Group Policy Editor by typing "gpedit.msc" in the Start menu search bar and pressing Enter.
Navigate to Computer Configuration > Administrative Templates > Windows Components > Windows Update > Configure Automatic Updates.
Set the policy to "Disabled".
Any available updates from Windows Update must be downloaded and installed manually, which you can do in the Settings app under Update & security > Windows Update.

Steps to Enable Auto Logon via the Windows Registry

Open the Registry Editor:

Press Win + R, type regedit, and press Enter.

Navigate to the Winlogon Key:

In the Registry Editor, go to:
plaintext
Copy code
HKEY_LOCAL_MACHINE\SOFTWARE\Microsoft\Windows NT\CurrentVersion\Winlogon

Set the DefaultUserName Value:

In the Winlogon key, look for a value named DefaultUserName.
If it exists, double-click it and set its value to your username.
If it doesn’t exist, right-click on the right pane, select New > String Value, name it DefaultUserName, and set it to your username.

Set the DefaultPassword Value:

Look for a value named DefaultPassword.
If it exists, double-click it and set its value to your password.
If it doesn’t exist, create it as a String Value in the same way as DefaultUserName, and set it to your password.

Set the AutoAdminLogon Value:

Look for a value named AutoAdminLogon.
If it exists, double-click it and set its value to 1.
If it doesn’t exist, create it as a String Value and set it to 1.

Set the DefaultDomainName Value (Optional):

If you are part of a domain, you should also add or edit the DefaultDomainName value to your domain name.
If not on a domain, you can set it to your computer’s name.

Restart Your Computer:

After making these changes, restart your computer. Windows should automatically log in to the specified user account.

Steps to Set Up a Batch File in the Startup Folder

Find the batch files in openems/AutoStartWindows

Place the Batch File in the Startup Folder:

Press Win + R, type shell:startup, and press Enter. This will open the Startup folder.
Copy your batch file into this folder.
Remember if you change the batch file in AutoStartWindows, you have to copy it to the Startup location (above)
What Happens
Auto Login: When the system starts, it will automatically log in to the specified user account.
Batch File Execution: After logging in, the batch file in the Startup folder will run, and a console window will be displayed.
Summary

By enabling auto login and placing your batch file in the Startup folder, your script will run automatically with a visible console window every time the system starts. This method is simple, effective, and ensures that your application runs as intended with a display.

## Leaf Contactor timing
	From LBC	From VCM
Timestamp	CAN ID	CAN ID	Byte	Bit	Description
5.891	1DB		3	5	LB_MainRelayOn_flag - give the ok to turn the main relay on 1=ok
6.398		1D4	5	6	Relay_Plus_Output_Status - 1=true
7.178		1D4	4	2	StatusOfHighVoltagePowerSupply 1=true

	Wait for 1DB lb LB_MainRelayOn_flag = true
	close precharge relay
wait 60ms
	close neg relay/contactor
	send 1D4 Relay_Plus_Outpu = true
wait 3 seconds
	close pos relay/contactor
	send 1D4 StatusOfHighVoltagePowerSupply = true
wait 300ms
	open precharge relay

## Leaf Battery Data Sources
	Msg Name	CAN Msg	Byte	SavvyCan Name or comment
Failsafe Status
Contactor Status
Voltage	BatteryStatus	1DB	0,1	LB_Total_Voltage
Current	BatteryStatus	1DB	2,3	LB_Current
Temperature	LBC_Data_Reply	7BB		extracted from BatteryStatus GROUP_PACK_TEMPERATURES
SOC	BatteryStatus	1DB	4	LB_Usable_SOC
SOH	LBC_Data_Reply	7BB	28	extracted from GROUP_BATTERY_STATE
Energy Remaining				calculated from m_capacity_kwh (below) * m_soc_percent (SOC above, ie usable SOC)
Capacity	LBC_Data_Reply	7BB	35	calculated from m_capacity_kwh = (24kWh * SOH)
Max Charge Voltage				constant = CRITICALLY_HIGH_VOLTAGE * NUM_CELLS (4.15v * 96)
Min Charge Voltage				constant = CRITICALLY_LOW_VOLTAGE * NUM_CELLS (3.0 * 96)
Max Charge Current				calculated from voltage and charge power limit
Max Discharge Current				calculated from voltage and discharge power limit

Max Charge Power	LBC_Power_Limits	1DC	1,2
Max Discharge Power	LBC_Power_Limits	1DC	0,1

## IP Addresses
192.168.2.10	wired	Sinexcel Inverter
192.168.2.11	wired	Installed Pi (6)
192.168.2.12	wired	Test Pi (9)
192.168.2.14	wired	Windoze backend server
192.168.2.1

## Gradle
Compiling with 'gradle'
-this was working but as of this writing doesn't work again... not sure if it has to do with it depending on things built by Eclipse or VSCode? More work needed (UNFORTUNATELY)

Install Gradle
https://gradle.org/install/

Command needed to make gradle available on the command line
export PATH=$PATH:/opt/gradle/gradle-8.7/bin

Meager Instructions from OEMS on how to compile
https://openems.github.io/openems.io/openems/latest/backend/build.html

Commands...
gradle buildBackend
gradle buildEdge

## Force Recompile
In Github Desktop
Remove repository using Github Desktop
right click on the name in the top right corner and choose remove, click move to trash, click Remove					Do the below proceedure if you get 100+ errors, etc for no apparent reason.

Click in the top left, click Add, select Clone
Click URL
Paste in the URL in form https://github.com/JimsterCoder/openems
Fix the name in the local path, as requred
Click Clone
Wait...
Select "For my own purposes"
Click Continue
Change to your desired Branch
Click Fetch

Open Eclipse
File->Switch Workspace->Other
Select the directory of the repository you cloned above
Click Launch
Close the Welcome window (if applicable)
Menu: File → Import…​ → Bndtools → Existing Bnd Workspace →Next>
Your source code directory should have been selected as Root Directory automatically → Finish → "Switch to Bndtools perspective?" Yes
Wait...
Wait more.. until all is quiet in the bottom right corner.

Click io.openems.backend.application
Double-click BackendApp.bndrun
etc..
Click io.openems.edge.application
Double-click EdgeApp.bndrun
etc..

## OEMS Scheduler
How to use OEMS "Scheduler Daily"

	1	Remove all schedulers (ie Scheduler All Aphabetically)

	2	Create all the componets you want to schedule and make sure they are enabled
		Examples:
		ctrlBalancing0 - a balancing controller to buy/sell 0 power
		ctrlFixActivePower0 - to turn the inverter 'off'
		ctrlFixActivePowerBuy10kW - to charge the battery at 10kW

	3	Use a text editor to create a file in the follow format
		[{ "time": "00:00:00", "controllers": [ "ctrlBalancingRESTapi"] },
		{ "time": "01:00:00", "controllers": [ "ctrlFixActivePower0"] },
		{ "time": "07:00:00", "controllers": [ "ctrlBalancingRESTapi"] },
		{ "time": "09:00:00", "controllers": [ "ctrlFixActivePower0"] },
		{ "time": "17:00:00", "controllers": [ "ctrlBalancingRESTapi"] },
		{ "time": "21:00:00", "controllers": [ "ctrlFixActivePower0"] },
		{ "time": "21:59:00", "controllers": [ "ctrlFixActivePowerHOP"] },
		{ "time": "22:59:55", "controllers": [ "ctrlBalancingRESTapi"] }]

		The scheduler will trigger the listed controler at the listed time and will keep that controller on until the next time setting.

	4	Login to the Edge Apache Felix, create the Scheduler Daily component and past in the text from above for the schedule.

## 3ph neutral test
Monday, August 5, 2024	9:30-10-30am
Conducted test to see how much current flows in the 3phase netural wire on the Sinexcel inverter

First, verified meter by connecting CT to the solar output line and see that the reading is the same as the inline meter which measures the solar output.
Ramped output from 10kW to -10kW and injected random unbalanced load between 2kW and 4 kW on phases 1 and 2.
Max current observed, only 1 reading of 1 second, was 60w. During ramping readings between 20-40w. Once stable, readings between 0-20w.
Readings always postive (consuming power).
No noticiable change when adding or removing load.

Graph of measure neutral current below. 9-10pm charging at 18 kW. 11-12pm unbalanced load, 6:30am 11kW nearly balanced load.
(note that the scale is Watts, not kW, as indicated)